NetXMS User ManualSolution Guide

NetXMS Solution Guide
Table of Contents

31
Introduction


42
Uninterruptible Power Supply (UPS) Monitoring


42.1
UPS Monitoring Basics




1 Introduction 

This manual is intended for both NetXMS administrators and users, and provides various scenarios and useful hints of NetXMS configuration to help network administrator configure he's monitoring system. It's assumed that you are using NetXMS Console for Windows (nxcon.exe).

2 Uninterruptible Power Supply (UPS) Monitoring
2.1 UPS Monitoring Basics
You can monitor UPS devices attached to the hosts via serial cable or USB via UPS subagent. Once you have your UPS attached to the host and NetXMS agent installed, you should configure UPS subagent. First, add the following line to agent's configuration file main section:
SubAgent = ups.nsm

on Windows or

SubAgent = agent_install_prefix/lib/libnsm_ups.so

on UNIX. Second, configure attached UPS devices. Create "UPS" section, and for each UPS device attached to the host add line in the following format:
Device = id:port:protocol
where id is a number in range 0 .. 127 which will be used in requests to identify device; port is a communication port for serial connection or UPS serial number for USB connection; and protocol is a communication protocol used by connected device. Protocol can be either APC (for APC devices), BCMXCP (for devices using BCM/XCP protocol – for example, HP, Compaq, or PowerWare devices), or USB for USB-attached devices. Below is an example of UPS configuration section for two devices attached via serial ports, one is APC device (configured as device 0) and one is HP device (configured as device 1):
# UPS subagent configuration section

*UPS

Device = 0:/dev/ttyS0:APC

Device = 1:/dev/ttyS1:BCMXCP

Once UPS subagent is configured, you can start to monitor UPS devices status via parameters provided by it:
	Parameter
	Type
	Meaning

	UPS.BatteryLevel(*)
	Integer
	Battery charge level in percents.

	UPS.BatteryVoltage(*)
	Float
	Current battery voltage.

	UPS.ConnectionStatus(*)
	Integer
	Connection status between agent and device. Can have the following values:
0

Agent is communication with the device

1

Comunication with the device has been lost



	UPS.EstimatedRuntime(*)
	Integer
	Estimated on-battery runtime in minutes.

	UPS.Firmware(*)
	String
	Device's firmware version.

	UPS.InputVoltage(*)
	Float
	Input line voltage.

	UPS.LineFrequency(*)
	Integer
	Input line frequency in Hz.

	UPS.Load(*)
	Integer
	Device load in percents.

	UPS.MfgDate(*)
	String
	Device manufacturing date.

	UPS.Model(*)
	String
	Device model name.

	UPS.NominalBatteryVoltage(*)
	Float
	Nominal battery voltage.

	UPS.OnlineStatus(*)
	Integer
	Device online status. Can have the following values:
0

Device is online.

1

Device is on battery power.

2

Device is on battery power and battery level is low.



	UPS.OutputVoltage(*)
	Float
	Output line voltage.

	UPS.SerialNumber(*)
	String
	Device's serial number.

	UPS.Temperature(*)
	Integer
	Internal device temperature.


Please note that not all parameters supported by all UPS devices. Many old or simple models will support only basic things like UPS.OnlineStatus parameter.
Most tipical approach is to monitor UPS.OnlineStatus for going to 1 or 2, and then send notifications to administrators and shutdown affected hosts if needed. You can also monitor UPS.EstimatedRuntime parameter for the same purposes if your devices support it.

2.2 Simple Scenario

Consider the following simple scenario: you have two servers, Node_A and Node_B, connected to one UPS device. UPS device is APC Smart UPS 1700, connected with serial cable to Node_A on first COM port. Both nodes are running Windows operating system. You need to notify administrator if UPS goes to battery power, and shutdown both nodes in case of low battery condition. We assume that both nodes have NetXMS agent installed.
To accomplish this, do the following:

Step 1.

Configure UPS monitoring subagent on Node_A. Add the following line to main agent's config section:

SubAgent = ups.nsm

At the end of configuration file, create UPS subagent configuration section:

# UPS subagent configuration section

*UPS

Device = 0"COM1:":APC
Step 2.
	© 2003 — 2006 NetXMS Team
	Version 0.2.12


5

